Date:	June 5, 2008
Vendor Name:		BACnet Stack hosted on SourceForge.net
Product Name:		Simple Sensor
Product Model Number:			GNU
Applications Software Version:					Firmware Revision:	1.00
BACnet Protocol Revision:				5

Product Description:
Smart sensor

BACnet Standardized Device Profile (Annex L)
	BACnet Operator Workstation (B-OWS)
	BACnet Building Controller (B-BC)
	BACnet Advanced Application Controller (B-AAC)
	BACnet Application Specific Controller (B-ASC)
X	BACnet Smart Sensor (B-SS)
X	BACnet Smart Actuator (B-SA)

List all BACnet Interoperability Building Blocks supported (see Annex K in BACnet Addendum 135d):
DS-RP-B Read Property / DS-WP-B Write Property / DM-DDB-B Dynamic Device Binding

Which of the following device binding methods does the product support? (check one or more)
	Send Who-Is, receive I-Am (BIBB DM-DDB-A)
x	Receive Who-Is, send I-Am (BIBB DM-DDB-B)
	Send Who-Has, receive I-Have (BIBB DM-DOB-A)
	Receive Who-Has, send I-Have (BIBB DM-DOB-B)
	Manual configuration of recipient device's network number and MAC address
	None of the above

Standard Object Types Supported:

Analog Value Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:

	4. List of all properties that are writable where not otherwise required by this standard
Present_Value
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions
Present Value		0.0 – 100.0, resolution of 1.0.
Object_Name		20 character limit

Binary Value Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:

	4. List of all properties that are writable where not otherwise required by this standard
Present_Value
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning

	6. List of any property value range restrictions:
Property Identifier		Restrictions

Device Object Type
	1. Dynamically creatable using BACnet's CreateObject service?			No
	2. Dynamically deletable using BACnet's DeleteObject service?			No
	3. List of optional properties supported:

	4. List of all properties that are writable where not otherwise required by this standard
Object_Name / Max_Master / Max_Info_Frames
	5. List of proprietary properties:
Property Identifier		Property Datatype	Meaning
9600		Unsigned	Baud Rate

	6. List of any property value range restrictions:
Property Identifier		Restrictions
Object_Name		< 20 characters
Max_Master		1-127
Max_Info_Frames		1-255

Data Link Layer Options (check all that are supported):

	BACnet IP, (Annex J)
	BACnet IP, (Annex J), Foreign Device
	ISO 8802-3, Ethernet (Clause 7)
	ANSI/ATA 878.1, 2.5 Mb. ARCNET (Clause 8)
	ANSI/ATA 878.1, RS-485 ARCNET (Clause 8), baud rate(s):
X	MS/TP master (Clause 9), baud rate(s):	9600, 19200, 38400, 57600, 76800
	MS/TP slave (Clause 9), baud rate(s):
	Point-To-Point, EIA 232 (Clause 10), baud rate(s):
	Point-To-Point, modem, (Clause 10), baud rate(s):
	LonTalk, (Clause 11), medium:
	Other:

Networking Options (check all that are supported):

Router, Clause 6 - List all routing configurations (e.g. ARCNET-Ethernet, Ethernet-MS/TP, etc.):

Annex H.3, BACnet Tunneling Router over UDP/IP
BACnet/IP Broadcast Management Device (BBMD)
BBMD supports registrations by Foreign Devices

Segmentation Capability (check all that apply):
	Window Size
Segmented requests supported
Segmented responses supported

Character Sets Supported (check all that apply):
Indicating support for multiple character sets does not imply that they can all be supported simultaneously.

x	ANSI X3.4
	IBM/Microsoft DBCS
	ISO 8859-1
	ISO 10646 (UCS-2)
	ISO 10646 (ICS-4)
	JIS C 6226

If this product is a communication gateway, describe the non-BACnet equipment/network(s) that the gateway supports:
N/A

Include any addition information about the product's BACnet capabilities relevant to interoperability: